| Safety | SOSO | Revision Date: 05/20/19 Revision #: 4 By: M. Heinold |
| --- | --- | --- |
| Verified by:___ Date:_________ | Plant Fixed Detectors (Cross Sensitivity) |  |
| Date Reviewed: 05/20/19 | I-D-05.61 Page 1 of 14 | Original Issue: 6/8/98 Originator: P. Daigle |

STATEMENT OF PROCEDURE

There are several types of fixed detectors at the site; AN, HCN, NH3, O2, CL2, SO2, LEL, H2.  The HCN, Ammonia, Sulfur Dioxide, Chlorine and Acrylonitrile Detectors have a cross sensitivity to other gases.  Below is a listing of the type of fixed detector and the gases in which a cross sensitivity exists.  Attached is also a list of all the detectors with their locations.  Records of calibrations and maintenance can be found in the I&E Shop or on the Beamex calibration database.  Historical data can be found at the following:  G:\I&E\Detectors\Historical Data.

The contents of this procedure meets all requirements of the Ineos 20 Principles for Behavioral Safety and Process Safety Management as detailed in SOSO I-A-01.06.

PROCEDURE

HCN detectors: [Alarm setpoint 4.7 ppm]

This gas	In this

concentration	Will cause sensor to show

Ammonia	100 ppm	  1 ppm ** May alarm at 500 ppm Ammonia

Chlorine	10 ppm	  1 ppm (-)

Hydrogen chloride	16 ppm		3 ppm

Carbon dioxide	30% Vol		1 ppm

Carbon monoxide	1000 ppm		5 ppm

Methane	100% Vol		1 ppm

Propane	1% Vol		1 ppm

Sulfur dioxide	10 ppm	 	23 ppm ** May alarm at 2 ppm SO2

Hydrogen sulfide	20 ppm		110 ppm ** May alarm at 1 ppm, H2S can occur in sewers

Nitrogen dioxide	20 ppm		35 ppm (-)

Hydrogen	1.5% Vol		40 ppm

Ethylene or Propylene	12,000 ppm		50 ppm ** This is more sensitive than LEL detectors

Ammonia detectors [Alarm setpoint 35 ppm]

This gas	In this

concentration	Will cause sensor to show

Chlorine	10 ppm		1 ppm

Hydrogen cyanide	50 ppm		10 ppm ** May alarm at 175 ppm HCN

Carbon dioxide	1% Vol		10 ppm

Carbon Monoxide	200 ppm		5 ppm

Methane	100% Vol		10 ppm

Methanol	200 ppm		4 ppm

Sulfur dioxide	20 ppm		1 ppm

Hydrogen sulfide	20 ppm		70 ppm ** May alarm at 10 ppm, H2S can occur in sewers

Nitrogen dioxide	20 ppm		15 ppm (-)

Nitrogen monoxide	30 ppm		10 ppm

Hydrogen	1000 ppm		10 ppm

Sulfur Dioxide (SO2) Detectors {Alarm setpoint 5 ppm]

This gas	In this

concentration	Will cause sensor to show

Ammonia	50 ppm	2 ppm ** May alarm at 125 ppm

Dimethyl disulfide	50 ppm	50 ppm

Dimethyl sulfide	50 ppm	50 ppm

Ethylene (&Propylene?)	200 ppm	1 ppm ** May alarm at 1000 ppm

Acetylene	25 ppm	30 ppm ** May alarm at 4 ppm Acetylene

Carbon dioxide	30% Vol	1 ppm

Carbon monoxide	3000 ppm	1 ppm

Methane	2% Vol	1 ppm

Methyl Mercaptan	12 ppm	30 ppm** May alarm at 2 ppm, Odorant in propane & natural gas

Propane	1% Vol	1 ppm

Hydrogen sulfide	6 ppm	30 ppm ** May alarm at 1 ppm, H2S can occur in sewers

Nitrogen dioxide	20 ppm	20 ppm (-)

Nitrogen monoxide	20 ppm	0.4 ppm

Hydrogen 	0.5% Vol	1 ppm

Chlorine (CL2) Detectors [Alarm setpoint 1 ppm]

This gas	In this

concentration	Will cause sensor to show

Ammonia	50 ppm	0.4 ppm ** May alarm at 125 ppm NH3

Hydrogen chloride	15 ppm	1 ppm

Carbon dioxide	0.5% Vol	0.02 ppm

Carbon monoxide	100 ppm	0.02 ppm (-)

Methane	2% Vol	0.02 ppm

Sulfur dioxide	5 ppm	5 ppm ** May alarm at 1 ppm SO2

Hydrogen sulfide	10 ppm	5 ppm ** May alarm at 2 ppm, H2S can occur in sewers

Nitrogen dioxide	5 ppm	1 ppm

Hydrogen	1000 ppm	0.5 ppm

Acrylonitrile (AN) Detectors [Alarm setpoint 25 ppm]

This gas	In this

concentration	Will cause sensor to show

Chlorine	3 ppm	0 ppm

Carbon Monoxide	20 ppm	200 ppm

Hydrogen Chloride	15 ppm	15 ppm

Ammonia	75 ppm	0 ppm

Methane	4000 ppm	0 ppm

Ethyl Alcohol	40 ppm	20 ppm

Ethylene	20 ppm	20 ppm

Iso Butin	4000 ppm	0 ppm

ACRYLONITRILE  DETECTORS

DETECTOR #	TAG#			LOCATION

1.			UA-71646		N. Side of “B” AN Stg. Tank

2.			UA-71647		N. Side of “A” AN Stg. Tank

3.			UA-71648		S. Side of “D” AN Stg. Tank

4. 			UA-71649		S. Side of “C” AN Stg. Tank

5.			AE-71100		Acrylo Pipeline Metering Skid

6.			AE-75400		Acrylo Pipeline Pigging Skid

7.			AE-75401		Acrylo Pipeline Pigging Skid

PORT

1P.			AE-74975		NH3 Process Area.

2P. 		AE-74976		Acrylo Product Tanks

3P.			AE-74977		Acrylo Loading Pump

4P.			AE-74978		Acrylo Barge Dock

5P.			AE-74979		Acrylo Barge Dock

7P.			AE-74981		Acrylo Ship Loading Pier

9P.			AE-74983		Acrylo Tank Entrance Road

AMMONIA  DETECTORS

DETECTOR #	TAG#			LOCATION

ACRYLO  AREA

1.			UA-04801		N. E. of NH3 Vaporizers

2.			UA-04802		S.W. of NH3 Vaporizers

CB&I  AREA

3.			UA-71801		N.E. of  T-1 NH3 Stg. Tank

4. 			UA-71802		Top of  T-1 NH3 Stg. Tank

5.			UA-71803		S.W. of  T-1 NH3 Stg. Tank

6.			UA-71804		N. Top of Platform at Relief Valves

7.			UA-71805		S. Top of Platform at Relief Valves

8.			UA-71806		North of T-2

9. 			UA-71807		West of T-2

10.			UA-71808		North NH3 Compressor Shed

11.			UA-71809		South NH3 Compressor Shed

14.			UA-71612		West of T-1 on Dike

15.			UA-71613		North of T-1 on Dike

16.			UA-71614		East of T-1 on Dike

25.			AE/AT-75350		N.W. Fricke Condenser Skid

26.			AE/AT-75351		Fricke Compressor Skid

27.			AE/AT-75352		NH3 Pipeline Meter Skid

28.			AE/AT-75353		N. NH3 Pipeline Pigging Skid

29.			AE/AT-75355		S. NH3 Pipeline Pigging Skid

CONTROL ROOM  AREA

17.			UA-01645		Control Room Air Intake, South

18. 		UA-01650		Control Room Air Intake, South

23.			UA-01656		N.W. Side of Control Room

24.			UA-01657		N.W. Side of Control Room

RXR3  AREA

19.			UA-30601		North NH3 Feed Valves

20. 		UA-30602		South NH3 Feed Valves

21.			UA-30603		North Refrig Skid

22.			UA-30604		South Refrig Skid

RXR4  AREA

30.			UA-40601		NH3 Feed Valves

31. 		UA-40602		NH3 Feed Valves

32.			UA-40605		North Refrig Skid

33.			UA-40606		South Refrig Skid

BARGE DOCK  AREA

12.			UA-72801		T-Head West of Propylene Booster Pump

13. 		UA-72802		T-Head West of Ammonia Booster Pump

PORT  AREA

1P.			AE-74960		Top of NH3 Stg Tank

2P.			AE-74961		NH3 Pump Area

3P.			AE-74962		NH3 North Dike Entrance

4P.			AE-74963		NH3 East Dike Entrance

5P.			AE-74964		NH3 Process Area N.of Cond. Fans

6P.			AE-74965		NH3 Process Area Pigging Skid

7P.			AE-74966		NH3 Barge Dock East

8P.			AE-74967		NH3 Barge Dock West

10P.		AE-74969		Ship Pier

CHLORINE  DETECTORS

DETECTOR #	TAG#			LOCATION

1.			UA-76601		N.E. Corner Warehouse Bottle Rack

2.			UA-76602		N.W. Corner Warehouse Bottle Rack

3.			UA-76603		S.E. Corner Warehouse Bottle Rack

4. 			UA-76604		S.W. Corner Warehouse Bottle Rack

5.			UA-61603		N.E. Corner by Cylinders Raw Water Pond

6.			UA-61604		N.W. Corner by Cylinders Raw Water Pond

7.			UA-61605		S.E. Corner by Cylinders Raw Water Pond

8.			UA-61606		S.W. Corner by Cylinders Raw Water Pond

9.			UA-65622		N.E. Corner CT Cylinders

10.			UA-65624		S.E. Corner CT Cylinders

11.			UA-65625		N.W. Corner CT Cylinders

12.			UA-65626		S.W. Corner CT Cylinders

HCN  DETECTORS

DETECTOR #	TAG#			LOCATION

ACH  AREA

1.			UA-08617		2nd Level  North Holding Tank

2.			UA-08618		2nd Level  East Gen. Chiller

3.			UA-08619		3rd Level  East Generator

4. 			UA-08620		3rd Level  South Crude Filer

34.			UA-08630		2nd Level  Analyzer House

37.			UA-08631		Ground Level North of GA0832S

38.			UA-08632		Ground Level West of Caustic Skid

39.			UA-08633		Ground Level N.W. of 1st Stage Reboiler

40. 		UA-08634		Ground Level  South of AR Column

REC PUR / APU  AREA

5.			UA-05602		Purification Top Deck Product Column

27.			UA-05601		Aceto Heads Column

35.			UA-07601		APU 3rd Deck North

36.			UA-07602		APU Ground Level North

50.			UA-07616		APU Analyzer House

51.			UA-04601		Purification GC House

REACTOR  AREA

14.			UA-01646		RXR1 Analyzer House

15.			UA-02646		RXR2 Analyzer House

16.			UA-01645		RXR1 Mass Spec

17.			UA-02645		RXR2 Mass Spec

33.			UA-03603		Semi Works Analyzer House

54.			UA-30010		RXR3 Analyzer House

55.			UA-40010		RXR4 Analyzer House

TANK FARM  AREA

7.			UA-71633		HCN Storage  Northwest

8.			UA-71634		HCN Storage  Northeast

9.			UA-71635		HCN Storage  Southeast

10.			UA-71636		HCN Storage  Southwest

19. 		UA-71627		AN Crude Tank, Southeast

20. 		UA-71628		AN Crude Tank, Northeast

21. 		UA-71629		AN Crude Tank, Northwest

22. 		UA-71630		AN Crude Tank, Southwest

48. 		UA-71644		ACH Storage Tank, North

52. 		UA-71653		ACH Storage Tank FA-0810, North

53. 		UA-71654		ACH Storage Tank FA-0810, South

RAILRACK  AREA

11.			UA-73630		Railrack North

12. 		UA-73631		Railrack South

24.			UA-73626		Railrack House, West

DPT  AREA

28.			UA-91623		Polishing Filter Pumps

29. 		UA-91624		DE Filter North

30.			UA-91625		DE Filter South

31.			UA-91626		DW Sump Pit  at DE  Filter

32.			UA-91627		WD Sump Pit West of RXR1

BARGE DOCK  AREA

1A.		UA-72625		Prover Skid  South

2A. 		UA-72626		Center of T-Head

3A.		UA-72627		Propylene Booster Pump

CONTROL ROOM  AREA

13.			UA-01642		AN Control Room Air Intake  A/C Room

45.			UA-01651		AN Control Room  Air Inlet  Southwest

46.			UA-01660		AN Control Room  Northeast

47.			UA-01661		AN Control Room  Northwest

49.			UA-76613		AN Control A/C Room

23.			UA-71631		CB&I Substation West Side

25.			UA-61601		A&S Utility Shelter Area East Side

26.			UA-71632		Lab Building 106

LEL  DETECTORS

DETECTOR #	TAG#			LOCATION

CB&I  AREA

1.			UA-71604		S.E of T-103 on Berm

2.			UA-71605		West of T-102

3.			UA-71606		North of T-102

4.			UA-71607		North of T-104

5.			UA-71608		Northwest of T-103

6. 			UA-71608		Top of T-102

7. 			UA-71610		Top of T-103

8. 			UA-71611		Top of T-104

32.			UA-71639		East of MEOH Tank

33.			UA-71640		West of MEOH Tank

34.			UA-71641		Acetone Feed Pumps (GA-7117 / 7117S)

35.			UA-71642		North of Acetone Tank FB-7103C

36.			UA-71643		South of Acetone Tank FB-7103C

63.			AT-71801-2		Propylene Pump Panel CBI

68.  		AE/AT-71801-1		CBI  Control House

RAILRACK  AREA

9.			UA-73602		N.W. of Railrack C3 Compressors

10.			UA-73603		S.E. of Railrack C3 Compressors

11.			UA-73604		N.W. of  Truck Loading Rack

12. 		UA-73605		N.E. of  Truck Loading Rack

13. 		UA-73606		S.W. of  Truck Loading Rack

14. 		UA-73607		S.E. of  Truck Loading Rack

15. 		UA-73608		Btwn. Track 3&4, N. of Cntr. of Railrack

16. 		UA-73609		Btwn. Track 3&4, N. End of Railrack

17. 		UA-73610		Btwn. Track 3&4, Center of Railrack

18.			UA-73611		Btwn. Track 3&4, S. end of Railrack

19.			UA-73612		Btwn. Track 3&4, S. of Cntr. of Railrack

20.			UA-73613		Pipe Rack, W. of HCN Railcar Wash Stn.

21.			UA-73614		Pipe rack, North Railrack Parking Lot

22.			UA-73615		Field, far North of  C3 Compressors

23.			UA-73616		Intake of #3 Elliot Air Compressor

REACTOR  AREA

25.			UA-30603		N. RX3 Feed Control Valves

26.			UA-30604		S. RX3 Feed Control Valves

27.			UA-03609		N. Semi Works Startup Heater

28.			UA-03610		S. Semi Works Startup Heater

61.			UA-01663		RX1 Analyzer House

62.			UA-01668		RX1 Mass Spec

64.			UA-02668		RX2 Mass Spec

65.			UA-30009		RX3 Analyzer House

66.			UA-03643		SWR Analyzer House

67. 		UA-02663		RX2 Analyzer House

70.			UA-40603		RX4 Feed Control Valves

71.			UA-40604		RX4 Feed Control Valves

72.			UA-40009		RX4 Analyzer House

73.			UA-04803		S. C3 Vaporizers

74.			UA-04804		N. C3 Vaporizers

REC PUR / APU  AREA

45.			UA-07617		APU Analyzer House

46. 		UA-07618		APU Analyzer House **HYDROGEN**

47.			UA-04602		Purif. Analyzer House

48.			UA-04603		Purif. Analyzer House **HYDROGEN**

CONTROL ROOM  AREA

24.			UA-01648		South AN Control Room near Air Intake

29.			UA-01654		N.W. Corner Acrylo Control Room

30.			UA-01655		N.W. Corner Acrylo Control Room

31.			UA-01643		South AN Control Room near Air Intake

37.			UA-76609		AN Control A/C Room

38.			UA-76610		AN Control A/C Room

39.			UA-76611		AN Control Room Lab (High)

40.			UA-76612		AN Control House (High)

41.			UA-76614		East of AN Control Room

42.			UA-76615		East of AN Control Room

43.			UA-76618		AN Control Room Lab (Low)

44.			UA-76619		AN Control House (Low)

ACETO WAREHOUSE AREA

76.			AT-76620		S. Wall

77.			AT-76621		W. Drumming

78.			AT-76622		N. Wall

PORT  AREA

1P.			AE-74950		NH3 Heaters

2P.			AE-74951		Acrylo Combustion Unit

3P.			AE-74952		Acrylo Barge Dock

5P.			AE-74954		Ship Jetty

6P.			AE-74955		Ship Jetty

8P.			AE-74957		Natural Gas Inlet

9P.			AE-74958	 	Ship Pier Control Building Pres. Unit

10P.		AE-74959		Ship Pier Control Building Pres. Unit

OXYGEN DETECTORS

DETECTOR #	TAG#			LOCATION

1.			UA-07615		APU Analyzer House

2.			UA-04600		Acrylo GC Analyzer House

4. 			UA-01662		RXR1 Analyzer House

5.			UA-01667		RXR1 Mass Spec

6.			UA-02662		RXR2 Analyzer House

7.			UA-02667		RXR2 Mass Spec

8.			UA-30008		RXR3 Analyzer House

9.			UA-03645		SWR Analyzer House

10.			UA-40008		RXR4 Analyzer House

11.			UA-05380		HQ Shed

SO2  DETECTORS

DETECTOR #	TAG#			LOCATION

1.			UA-05805		N.W. of SO2 Coffins

2.			UA-05806		N.E. of SO2 Coffins

3.			UA-05807		S.E. of SO2 Coffins

4. 			UA-05808		S.W. of SO2 Coffins

5.			UA-05809		N.W. Side Level 4 Aceto Hds. Col.

6.			UA-05810		N.E. Side Level 5 “Top” Aceto Hds. Col.

7.			UA-05811		N.E. Side Level 6 Hds. Col.

8.			UA-07801		N. Side Grd. Level Col. #12 Aceto Purif.

9. 			UA-07802		N. Side Level 2 Aceto Purif.

10.			UA-07803		S.E. Side Level 2 Aceto Purif.

11.			UA-07804		N.E. Side Level 3 Aceto Purif.

12.			UA-07805		S.E. Side Level 3 Aceto Purif.

13.			UA-07806		E. Side Level 5 Aceto Purif.

14.			UA-07807		E. Side Level 6 Aceto Purif.

15.			UA-07808		N. 1st Level APU

16.			UA-07809		N. Ground Level APU

17.			UA-76605		N.E. of Warehouse Bottle Storage Area

18.			UA-76606		N.W. of Warehouse Bottle Storage Area

19.			UA-76607		S.E. of Warehouse Bottle Storage Area

20.			UA-76608		S.W. of Warehouse Bottle Storage Area

21.			UA-01652		S.E. of AN Control Room

22.			UA-01653		S.W. of AN Control Room

23.			UA-01658		N.E. of AN Control Room

24.			UA-01659		N.W. of AN Control Room