| Safety | SOSO | Revision Date: 08/05/20 Revision #: 8 By: C. Amerson |
| --- | --- | --- |
| Verified by:___ Date:_________ | Organic Contamination of Steam System |  |
| Date Reviewed: 08/05/20 | I-D-05.70 Page 1 of 5 | Original Issue: 03/26/91 Originator: P. Daigle |

STATEMENT OF PROCEDURE

Potential problem areas in the Plant are organic lines and vessels that can develop equal or greater pressures than the 50 psig steam system which can be used to clear the equipment of organic liquids and polymers.

Organics in the steam system can do severe damage to mechanical equipment, i.e. boilers, turbines and steam lines.

The contents of this procedure meets all requirements of the Ineos 20 Principles for Behavioural Safety and Process Safety Management as detailed in SOSO

I-A-01.06.

PROCEDURE

1.	When organics contaminate the steam system, the following conditions occur:

- Potential for chemical exposure to employee(s)

- Potential for fire(s)

- Boiler and condensate pH's decrease causing corrosion throughout the system.

- Conductivity increases causing deposits throughout the system to form.

- Foaming can occur causing false condensate flows and level indications.

2.	To eliminate organic contamination, the following steps must be taken immediately.  Note:  SOP 1-W-08.73 (Organic Contamination of the Steam System) has specific steps to be taken in the Acrylo Block.

a.	Notify area Shift Manager and the Production Manager or his designee immediately of the situation and eliminate the condition causing the contamination.

b.	Divert the 50 pound steam flash drum blowdown from the Cooling Tower to the waste drain system via the atmospheric flash drum.

c.	Depending on the degree of contamination, blowdown the reactor steam drums, boilers and condensate system to the waste drain.  Open live steam to the recovery column, the quench contactors, and the quench strippers.  Start 10,000 to 30,000 lb/hr to the AOGI's.

d.	Foam the waste drain system if necessary to reduce vapors and fire hazard.

e.	Steam traps with discharge to the ground must be checked for organics Acrylo, Aceto, HCN or whatever chemical contaminated the steam system if necessary steam trap should be blocked.

f.	Consideration must be given to cancel Hot Work Permit to reduce the fire hazard.  (Sound Alarm)

g.	Make a map (drawing) indicating the affected area(s) and develop a plan to continue to check these areas until it is considered "safe".

**NOTE:	B, C, & D are needed to minimize and/or eliminate atmospheric contamination.  DO NOT BLOWDOWN TO THE DITCH.

3.	To prevent steam contamination, one must consider the operational equipment needing use of the steam system other than NORMAL operation.

a.	Do not connect steam out lines to any equipment having higher or equal pressure which is in service such as closed vessels and pump discharge lines.

b.	Vessels requiring steam out must be de-pressured and properly vented to the process flare or the chemical drain prior to steaming.

c.	Pump discharge lines needing steaming must be isolated and de-pressured to the chemical drain prior to steaming.  Some of the common pumps having equal or greater pressure than the 50 pound steam system in the Acrylonitrile unit, Acetone Cyanohydrin unit, and Aceto Purification unit are listed on the following pages.  This list is not all inclusive and prior to connecting to any equipment not listed thought must be given to the pressure and service involved.

ACRYLONITRILE UNIT PUMPS	Pump No. 	Disch. Pres.

I.	Reactor Areas

A.	Process Condensate

1.	#1 Train	GA-102/S	150 psig

2.	#2 Train	GA-202/S	150 psig

3.	#3 Train	GA-3003/S	150 psig

B.	Rich Water (to Recovery)	Pump No. 	Disch. Pres.

1.	#1 Train	GA-103/S	160 psig

2.	#2 Train	GA-203/S	160 psig

3.	#3 Train	GA-3004/S	160 psig

4.	#4 Train	GA-4004/S	160 psig

C.	Stripper Bottoms

1.	#1 Train	GA-101/S	 50 psig

2.	#2 Train	GA-201/S	 50 psig

3.	#3 Train	GA-3002/S	 50 psig

4.	#4 Train	GA-4002/S	 50 psig

D.	High Volume Recirculation

1.	#1 Train	GA-104 A,B,C	 70 psig

2.	#2 Train	GA-204 A,B,C	 70 psig

3.	#3 Train	GA-3001 A,B,C	 70 psig

4.	#4 Train	GA-4001A,B,C	 70 psig

E.	Absorber Side System

1.	#3 Train	GA-3005/S	 80 psig

2.	#4 Train	GA-4005/S	 80 psig

II.	RECOVERY AREA

A.	Recovery Column

1.	Recovery Column Btms	GA-403/S	120 psig

2.	Lean Water Surge Drum	GA-405/S	280 psig

B.	Recovery Column Decanter

1.	Water Boot Side	GA-406/S	130 psig

2.	Organic Side	GA-407/S	 50 psig

C.	Aceto Fractionator

1.	Bottoms	GA-408/S	 75 psig

2.	Reflux		GA-409/S	 60 psig

III.	Purification Area 	Pump No. 	Disch. Pres.

A.	Heads Column Bottom	GA-501/S	 70 psig

B.	Product Column

1.	Product Col. Bottoms	GA-502/S	 80 psig

2.	Product Col. Vacuum Pot	GA-519	125 psig

Pump No.	Disc. Pres

C.	Purification Decanter

1.	Water Boot Side	GA-504	140 psig

2.	Organic Side	GA-505/S	 50 psig

D.	Aceto Heads Column (A/H) Area

1.	A/H Column Bottoms	GA-415X&SX	130 psig

2.	Aceto Side Draw	GA-416X&SX	140 psig

E.	Acrylo Rundown Tank Area

1.	Acrylo Transfer	GA-506/S	 50 psig

2.	Slop Water	GA-603	110 psig

3.	Waste Drain	GA-602S	150 psig

F.	Chemical Additives

*Positive displacement pumps are capable of very high discharge pressures

1.	HQ (Heads Col.)	GA-507	Variable

(Recovery Col.)	GA-507S	"  "

(Aceto Heads Col.)	GA-510&B	"  "

2.	MEHQ (Prod Col.)	GA-509&S	"  "

(Rndn Tanks)	GA-508	"  "

3.	Glycolic Acid

(Heads Col.)	GA-510&S	"  "

(Aceto Heads Col.)	GA-517	"  "

ACETONE CYANOHYDRIN UNIT

A.	Generator Circ. Pumps

GA-804/S	70 psig

B.	Dilute Filter Feed Pumps	GA-806/S	75 psig

C.	1st Stage Pumps 	Pump No. 	Disch. Pres.

1.	Feed Pump		GA-808/S	70 psig

2.	Hotwell Cond. Pump	GA-810/S	50 psig

3.	Bottoms Pumps	GA-809/S	70 psig

D.	2nd Stage Pumps

1.	Feed Pumps		GA-812/S	50 psig

2.	Bottoms Pumps	GA-814/S	55 psig

E.	HCN Refrig. Compressor		175 psig

F.	Acetone Flush Pumps

(Positive Disp.)			Variable

G.	All Pumps in the Aceto Unit.

- Crude Rerun Pumps