| Green Lake Site | SHE OPERATING ELECTRICAL BREAKERS Criticality: 3 Review Date: 01/15/24 Page 1 of 2 | I-D-05.90 Revision: #05 Revision Date: 07/08/13 Owner: HSEQ Manager |
| --- | --- | --- |

STATEMENT OF PROCEDURE:

This procedure covers the operation of all electrical switches or circuit breakers at Green Lake Complex.  The intent is to develop safe operating practices for all personnel at our facility.  There have been instances where failure of a breaker or switch has caused an electrical arc/explosion to occur.  Such failures could cause flash burns to anyone within ten feet of the failure.  Due to the potential for this occurrence the following procedure was developed.

The contents of this procedure meets all requirements of the Ineos 20 Principles for Behavioral Safety and Process Safety Management as detailed in SOSO I-A-01.06.

REFERENCES:

SOSO I-D-00.50  Stop Work Intervention

I.	PROCEDURE

1.	All switching of the Plant Power Distribution System (480 volt or greater) shall be performed by personnel determined to be qualified by the Green Lake Complex I&E Supervision.

2.	All switching of manually operated switchgear breakers in plant electrical substations shall be performed by qualified I&E personnel.  This applies to feeds to Motor Control Centers (MCC's) and tie-switches that can cause back feeds into MCC's.

3.	All other switching of electrical loads can be performed by supervision of the group which operates the equipment or their authorized representative.  This would normally include all MCC equipment and other motor starters in plant electrical substations except distribution feeds.

4.	Any switching or electrical systems that can have a significant impact on process areas must be well communicated between the work groups involved.  This includes but is not limited to switching on the Power Distribution System, critical instrument panels, battery chargers and other instrument power back up systems.

5.	Explosion proof breakers and switches are excluded from this procedure.

6.	If the normal switching of a breaker by external switches is not possible and the breaker needs to be operated by opening the door and manually operating it, the I/E supervisor will review the safety requirements necessary and provide approval for the action.

7.	Orange Warning signs are posted in each substation with the requirements pertaining to Flash Protection Boundary, Hazard Risk Category, and Incident Energy Range of that particular location. Please see attachment A for clothing required for Hazard Risk Category.

8.	Arc flash ratings are for exposed systems.  When a compartment is closed and the live equipment is not exposed, a reduction of the Hazard/Risk Category is allowed to be lowered one level.

II.	Safety Requirements

1.	Flash Protection Clothing will be visually inspected prior to each use, to verify there are no tears or holes in any equipment.  If there are problems, contact the Green Lake Complex Safety Dept. for replacement prior to use.

2.	Arc Flash rated protective clothing as required by NFPA 70E (Attachment A) will be worn in any of the following applications.  Clothing requirements should be selected based on the incident energy rating of the area.

a.	Switching any of the plant power distribution systems, unless they are operated from remote locations or safe distances.  (see Section IV)

b.	Opening and closing manually operated breakers above 480V in plant electrical substations.

c.	Racking in or out any 480 VAC or above manual or electrical operated distribution breaker. A distribution breaker does not include 480V Motor Control Center loads such as pumps, fans, lighting panels, receptacle panels, etc.

d.	Whenever maintenance has been performed on 480V and higher breakers and they are being reinstalled and energized.

3.	Whenever flash protection is required, a backup person must be utilized.  The backup person must be in flash protection also.

4.	Personnel operating electrical breakers, switches, contactors or motor starters, must stand to one side (if possible) while the device is being operated.

III.	Housekeeping

1.	At least two sets of the required PPE must be kept ready for use in most buildings that have one or multiple substations located in them.

2.	Flash Protection clothing will be returned to its proper location immediately after use.

3.	The Green Lake Complex Safety will be responsible for inspecting this equipment and insuring that it is suitable for use at least once per year.

IV.	Safe Electrical Distance Zone

See Attachment B

V.	Location of Flash Suits

Sub   1	CPL

Sub  10	Acrylo Main

Sub 103	Aceto Purification

Sub 108	Administration

Sub 106	C.B.I.

Sub  13	Barge Dock

Sub 105	Utility

Sub 104	#3 Reactor Area

Attachment A

Attachment B

Reviewer’s Approval

| Name | Title | Date |
| --- | --- | --- |
| Gerald Jurica | I/E Execution Supervisor | 11/16/23 |

Document Change History

| Revision Date | Version Number | MODB Number | Description of Change | Author |
| --- | --- | --- | --- | --- |
| 01/15/24 | 5 | 19665 | Reviewed with no revisions, 2022 Personal Safety Commitment Administrative/Format Updates: Pg. #1 Header, “Reviewer Approval”, and “Document Change History” updated to QPGL400, removed VTA questions, and added statement in Footer. | J. Shelton |